## Front Page
National Resource Adequacy Assessment 2024 Inputs and Assumptions Data - Ireland
Purpose: To invite input from stakeholders on the demand and generation data to be used in the National Resource Adequacy Assessment 2025-2034. The generation and demand forecast are being prepared based on the inputs and assumptions provided in the consultation paper. The starting point for preparing these forecasts is: - Generation Inputs is GCS 2023-2032 final input data. - Demand Inputs is aligned to the latest available information. For any questions on this data, please contact info@EirGrid.com, referencing the National Resource Adequacy Assessment 2025-2034 in the subject line.
Disclaimer: EirGrid Plc have followed accepted industry practice in the collection and analysis of data available. While all reasonable care has been taken in the preparation of this data, EirGrid are not responsible for any loss that may be attributed to the use of this information. Prior to taking business decisions, interested parties are advised to seek separate and independent opinion in relation to the matters covered by this report and should not rely solely upon data and information contained herein. Information in this document does not amount to a recommendation in respect of any possible investment. This document does not purport to contain all the information that a prospective investor or participant in the Single Electricity Market (SEM) may need.
Version History:
| Version | Description | Date
| 1 | Initial Publication for Consultation | XX/03/2024

## Demand Inputs - IE
Ireland Demand Modelling Inputs
Electric Vehicles
| Year | Number of Electric Vehicles |  |  |  | Electirc Mileage |  |  |  | Efficiency |  |  |  | Charging Profile Uptake
|  | BEV | PHEV | LGV | Bus | BEV | PHEV | LGV | Bus | BEV | PHEV | LGV | Bus | Simple | Smarter
| 2025 | 113592 | 61408 | 10000 | 300 | 16216 | 7621 | 22482 | 33604 | 0.166 | 0.084 | 0.259 | 1.369 | 65% | 35%
| 2026 | 142459 | 112728 | 18019 | 480 | 15567 | 7317 | 21846 | 33604 | 0.164 | 0.084 | 0.258 | 1.362 | 54% | 46%
| 2027 | 213070 | 149104 | 29104 | 690 | 14918 | 7012 | 21211 | 33604 | 0.163 | 0.083 | 0.256 | 1.356 | 43% | 57%
| 2028 | 317119 | 195850 | 43254 | 930 | 14270 | 6707 | 20576 | 33604 | 0.161 | 0.082 | 0.255 | 1.349 | 32% | 68%
| 2029 | 436375 | 242228 | 60469 | 1200 | 13621 | 6402 | 19940 | 33604 | 0.16 | 0.081 | 0.254 | 1.342 | 21% | 79%
| 2030 | 561173 | 283827 | 80750 | 1500 | 12973 | 6097 | 19305 | 33604 | 0.158 | 0.081 | 0.253 | 1.335 | 10% | 90%
| 2031 | 689179 | 319931 | 104096 | 1830 | 12973 | 6097 | 19305 | 33604 | 0.157 | 0.08 | 0.251 | 1.329 | 10% | 90%
| 2032 | 822782 | 351270 | 130507 | 2189 | 12973 | 6097 | 19305 | 33604 | 0.155 | 0.079 | 0.25 | 1.322 | 10% | 90%
| 2033 | 960473 | 377497 | 159983 | 2578 | 12973 | 6097 | 19305 | 33604 | 0.154 | 0.079 | 0.249 | 1.315 | 10% | 90%
| 2034 | 1100630 | 398440 | 192525 | 2997 | 12973 | 6097 | 19305 | 33604 | 0.153 | 0.078 | 0.248 | 1.309 | 10% | 90%
Charging Profile
| Hour | Passenger Vehicle |  |  |  | Light Goods Vehicle |  |  |  | Bus
|  | Weekday |  | Weekend |  | Weekday |  | Weekend |  | Weekday & Weekend
|  | Simple | Smarter | Simple | Smarter | Simple | Smarter | Simple | Smarter | Simple | Smarter
| 0 | 3.323% | 6.684% | 3.79% | 7.935% | 14.19% | 20.92% | 7.01% | 13.13% | 8.9% | 11.52%
| 1 | 2.169% | 7.089% | 2.919% | 8.147% | 12.29% | 18.13% | 6.076% | 11.38% | 8.7% | 11.26%
| 2 | 1.327% | 7.343% | 1.955% | 8.186% | 9.458% | 13.95% | 4.674% | 8.755% | 8.6% | 11.13%
| 3 | 0.8442% | 7.218% | 1.321% | 8.295% | 5.675% | 8.368% | 2.804% | 5.253% | 8.2% | 10.61%
| 4 | 0.6273% | 6.625% | 0.9702% | 8.125% | 0.7928% | 1.169% | 0.3918% | 0.7339% | 6.4% | 8.281%
| 5 | 0.5839% | 4.992% | 0.7715% | 5.922% | 0% | 0% | 0% | 0% | 6% | 7.764%
| 6 | 0.8572% | 3.449% | 0.6733% | 3.289% | 0% | 0% | 0% | 0% | 1.4% | 1.812%
| 7 | 2.01% | 2.527% | 0.7502% | 1.309% | 0% | 0% | 0% | 0% | 1.9% | 2.458%
| 8 | 4.292% | 2.591% | 1.168% | 0.9784% | 0% | 0% | 0% | 0% | 1.9% | 2.458%
| 9 | 5.383% | 3.249% | 1.93% | 1.347% | 0% | 0% | 0% | 0% | 1.9% | 1.054%
| 10 | 4.249% | 2.565% | 3.028% | 2.113% | 0.3964% | 0.2579% | 0.1959% | 0.1619% | 1.7% | 0.9427%
| 11 | 3.541% | 2.137% | 4.125% | 2.879% | 3.964% | 2.579% | 1.959% | 1.619% | 1.7% | 0.9427%
| 12 | 3.455% | 2.085% | 5.103% | 3.917% | 5.675% | 3.692% | 2.804% | 2.317% | 1.6% | 0.8873%
| 13 | 3.679% | 2.22% | 5.97% | 3.75% | 3.964% | 2.579% | 4.448% | 3.675% | 1.6% | 0.8873%
| 14 | 3.489% | 2.106% | 6.366% | 3.998% | 0.3964% | 0.2579% | 6.543% | 5.407% | 1.6% | 0.8873%
| 15 | 3.677% | 2.034% | 6.79% | 3.791% | 0% | 0% | 7.01% | 5.793% | 1.8% | 0.9982%
| 16 | 4.99% | 2.509% | 7.792% | 2.719% | 0% | 0% | 7.01% | 5.793% | 2.1% | 1.165%
| 17 | 6.708% | 2.53% | 8.372% | 2.921% | 0% | 0% | 7.01% | 3.505% | 2.4% | 1.2%
| 18 | 8.671% | 3.271% | 7.862% | 2.743% | 0% | 0% | 7.01% | 3.505% | 2.4% | 1.2%
| 19 | 9.098% | 4.576% | 7.181% | 2.505% | 0% | 0% | 7.01% | 5.793% | 3.4% | 1.885%
| 20 | 8.426% | 5.085% | 6.59% | 2.299% | 1.586% | 1.032% | 7.01% | 5.793% | 3.7% | 2.052%
| 21 | 7.341% | 5.169% | 5.753% | 3.613% | 13.24% | 8.614% | 7.01% | 5.793% | 4.9% | 2.717%
| 22 | 6.276% | 5.681% | 4.923% | 3.779% | 14.19% | 9.229% | 7.01% | 5.793% | 8.6% | 4.769%
| 23 | 4.984% | 6.266% | 3.897% | 5.439% | 14.19% | 9.229% | 7.01% | 5.793% | 8.6% | 11.13%
Heat Pumps
| Year | Installations |  | Efficiency | Annual Heating Demand
|  | Domestic | Commercial |  | Domestic | Commercial
| 2025 | 215000 | 25080 | 2.49 | 7.909 | 58.354
| 2026 | 283714 | 32200 | 2.54 | 7.909 | 58.354
| 2027 | 364571 | 39780 | 2.59 | 7.909 | 58.354
| 2028 | 457571 | 44840 | 2.64 | 7.909 | 58.354
| 2029 | 562714 | 48000 | 2.69 | 7.909 | 58.354
| 2030 | 680000 | 50000 | 2.74 | 7.909 | 58.354
| 2031 | 797286 | 52000 | 2.74 | 7.909 | 58.354
| 2032 | 914571 | 54000 | 2.74 | 7.909 | 58.354
| 2033 | 1031857 | 56000 | 2.74 | 7.909 | 58.354
| 2034 | 1149143 | 58000 | 2.74 | 7.909 | 58.354
Heat Pump Demand Profile
| Hour | Proportion of Daily Heat Demand (before temperature factored in)
| 0 | 2.341%
| 1 | 2.517%
| 2 | 2.58%
| 3 | 2.763%
| 4 | 3.178%
| 5 | 3.432%
| 6 | 4.121%
| 7 | 5.575%
| 8 | 5.766%
| 9 | 5.463%
| 10 | 4.878%
| 11 | 4.324%
| 12 | 4.154%
| 13 | 4.165%
| 14 | 4.062%
| 15 | 4.177%
| 16 | 4.498%
| 17 | 5.025%
| 18 | 5.184%
| 19 | 5.073%
| 20 | 4.842%
| 21 | 4.707%
| 22 | 4.277%
| 23 | 2.899%
Residential
| Year | Proportion of Homes on smart tariffs |  | Personal Consumption Growth Forecast |  | Efficiency Improvement
| 2025 | 45.44% |  | 2.5% |  | 1.5%
| 2026 | 56.35%
| 2027 | 67.27%
| 2028 | 78.18%
| 2029 | 89.09%
| 2030 | 100%
| 2031 | 100%
| 2032 | 100%
| 2033 | 100%
| 2034 | 100%
Commercial & Industrial
| Year |  | GNI* Growth Forecast
| 2025 - 2034 |  | 3%

## Generation Inputs - IE
Ireland Generation Modelling Inputs
Existing In-Market Conventional Generation Portfolio
Rated Capacity (MW)
| Plant Name | ID | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Aghada | AT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AT2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AT4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AD2 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
| Ardnacrusha | AA1 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | AA2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | AA3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | AA4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Dublin Bay | DB1 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
| Dublin Waste | DW1 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
| Edenderry | ED1 | 118 | 118 | 118 | 118 | 118 | 118 | 0 | 0 | 0 | 0
|  | ED3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
|  | ED5 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
| Erne | ER1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | ER2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | ER3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | ER4 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
| Great Island CCGT | GI4 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464
| Huntstown | HNC | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
|  | HN2 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
| Indaver Waste | IW1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
| Lee | LE1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LE2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | LE3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Moneypoint | MP1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MP3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liffey | LI1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LI2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LI3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | LI4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Poolbeg CC | PBA | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
|  | PBB | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
| Rhode | RP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | RP2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Sealrock | SK3 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
|  | SK4 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
| Tawnaghmore | TP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | TP3 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Tynagh | TYC | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
| Whitegate | WG1 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
New In-Market Conventional Generation Portfolio
Cumulative Rated Capacity (MW)
|  | Plant Name | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Gas Turbine Auction Results [1] | 1100 | 1210 | 2480 | 2540 | 2540 | 2540 | 2540 | 2540 | 2540 | 2540
|  | GCS 2023 Risk Adjusted Delivery | 530 | 820 | 820 | 1390 | 1390 | 1390 | 1390 | 1390 | 1390 | 1390
[1] Total capacity from approved capacity auction results which has not been issued with a termination notice.
Note: Values rounded to the nearest 10 MW.
Energy Storage Portfolio
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Rated Capacity (MW) | 1100 | 1140 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
|  | Energy Storage (MWh) | 2630 | 2720 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280
Note: Values rounded to the nearest 10 MW.
Demand Side Unit Portfolio
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Rated Capacity (MW) | 730 | 660 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750
Note: Capacity values rounded to the nearest 10 MW.
Interconnection Portfolio
Net Transfer Capacity (MW) [2]
|  | Unit | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Import | EWIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Greenlink [3] | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Celtic [3] | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
|  | North - South | 300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
| Export | EWIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Greenlink [3] | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Celtic [3] | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
|  | North - South | 300 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
[2] Rated transfer capacity to be used in economic dispatch model.
[3] Interconnector has not yet been commissioned.
Wind and Solar Portfolio
Rated Capacity (MW)
|  | Source | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Offshore Wind | 30 | 30 | 30 | 730 | 2870 | 5000 | 7140 | 9270 | 9270 | 9270
|  | Onshore Wind | 5110 | 5760 | 6400 | 6700 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000
|  | Solar | 2440 | 3090 | 3740 | 4330 | 4910 | 5500 | 6090 | 6670 | 6670 | 6670
Note: Capacity values rounded to the nearest 10 MW.
Other RES / Other Non-RES Portfolio
Rated Capacity (MW)
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Industrial | INDU | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Small Scale Hydro | SSH | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Conventional CHP | CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
| Landfill Gas | LFG | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| CHP_Bio | CHP Bio | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30

## Generation Availability
All Island Plant Performance Modelling Inputs
Availability Statistics
| Technology Category | Forced Outage Rate (%) | Scheduled Outage Duration (hours) | Annual Availability (%)
| DSU | 71.6 | - | 28.4
| DSU Run Hour Limited | 71.8 | - | 28.2
| Gas Turbine | 8.9 | 470 | 85.8
| Hydro | 10.9 | 470 | 83.7
| Steam Turbine | 11.3 | 820 | 79.3
| Interconnector* | 4.5 | 340 | 91.7
| Pumped Hydro Storage | 2.7 | 650 | 89.9
| System Wide | 19.2 | 680 | 73.1
* Statistics provided by the Regulatory Authorities
Note: The statistics in the table above are reflective of 2019-2023 data.